Production Specification

Product name:	ELECTRIC HEATER

Model:		DEH - 4HP

Specification:	3Φ 380V 12KW (12 KW *1 STEP)

Drawing No.:	DSH011208A

Date: 		Feb. 08, 2002

For the attention of:

| Prepared by | Reviewed by | Approved by |
| --- | --- | --- |

Product: ELECTRIC HEATER

Date: Feb. 08, 2002

1.Application

This specification shall be applied to the electric heater(s) for                               .

| Product Item |  | ELECTRIC HEATER |
| --- | --- | --- |
| Rate voltage |  | 3 380 V |
| Power capacity |  | 12 KW (1 STEP) |
| Standard resistance (Per step) |  | 24.06 Ω |
| Rated current (per step) |  | 18.2 A |
| Heater spec. / ea |  | 1000 W/EA |
| 2.Material of Components- Heater |  |  |
| Item |  | Material |
| Heater pipe | Φ8 | SUS 304 ф9.5 mm should be compressed to ф8 mm. |
|  | Φ11 | SUS 304 ф12.7 mm should be compressed to ф11 mm. |
|  | Φ14 | SUS 304 ф15.88 mm should be compressed to ф14 mm. |
| Heat dissipation fins |  | SUS 430 0.4t*9mm (0.4t *5mm in case of Φ8) |
| Insulation material |  | Should contain MgO more than 96% and should be “high MgO” suitable for high temperature or equivalent. |
| Heating element |  | Type FC-1 KANTAL D or equivalent. |
| Terminals & nuts |  | SS41 |
| Insulators |  | Ceramic insulator that can withstand high temperature (1500ºC). |
| Unit case |  | SGCC 1.2t. |
| Heat resistant cable |  | Heat resistant cable (GB WIRE / TEFRON WIRE). |
| Bimetal |  | An automatic return type (90ºC off/75ºC on) and a non-automatic type 120ºC should be connected in series. |
| Bushing |  | Bushing made of silicon that can withstand heat (200ºC). |
| Waterproof treatment |  | ShinEtu KE441T. |

3.Technological Level of Electric Heater

3-1  Insulation resistance test

The resistance between the filled part and non-filled part measured at room temperature should be 100MΩ or up.

3-2  Voltage withstanding test

Should withstand AC 1800V/min with no abnormality. (leakage current at room temperature 5mA)

3-3  Power consumption test

When the rated voltage is applied, power consumption should be within +5% to -5% of the rated power.

3-4  Repetitive power on-off test (for development tests only)

Under windy condition, apply 120% of the rated voltage for 30 minutes and power down for 15 minutes. Repeat the cycle 300 times. After the completion of the said test, the product should satisfy the requirements of abovementioned insulation resistance test, voltage withstanding test, and power consumption test.

  - Prevention of vibration and impact

No parts nor components should  be loosened or distorted because of vibration.

4. Other Subjects

4-1  Documents to be submitted

- Production specification

- Test report

- Drawings

4-2  Appearance

Should be free of any defect such as scratch or crack that may deteriorate performance

4-3  Packing

Should not cause any damage to the product during transportation, movement or handling and should carry necessary information such as capacity and product type on the surface of the packing.

5-4  Marking

Should show drawing numbers, power supply, capacity, manufacturer, etc. by use of AL stickers.

4-5 Heater protection device

Should install a T/C for the prevention of overheating. (should be indicated on the drawings.)

EHC Test Report

Product: ELECTRIC HEATER

Date: Feb. 098, 2002

For the attention of

-------------------------------

* Test items

| Product | DEH-4HP | P / NO | DSH011208A |
| --- | --- | --- | --- |
| Specification | 3Φ 380V 12 KW | Temp & Humidity | Room temperature |
| Step / Connection | 12 kW * 1 Step Y Connection | No. of samples | 1 set |

* Test Options

| Item | Criteria | Test method | Test result | Pass/Fail |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | Pass | Fail |
| Insulation resistance | Heater frame100 MΩ or up | 500V megger | ∞ | O |  |
| Withstanding voltage | Heater frame 1500V / min | 5000V withstanding voltage tester | Withstanding | O |  |
| Capacity (per step) | 12kw (resistance 22.9 - 25.2 ) + 5 % ~ - 5 % | Digital tester | 12.1 KW | O |  |
| Length | Dimension by the drawings | Within tolerable error | Within the range | O |  |

* Random Testing

| kW Item | Insulation resistance | Withstanding voltage | Capacity | Remark |
| --- | --- | --- | --- | --- |

| * Note. Besides, no scratch, crack or warpage should be noticeable. Prepared by | Reviewed by | Approved by |
| --- | --- | --- |